## CWR
Table: Scheme Supply Schedule and Water Balance Analysis
Crops/Month | J | F | M | A | M | J | J | A | S | O | N | D | Mean/sum | Remark
Maize 1 | 0 | 0 | 0 | 10.9 | 33.6 | 32 | 0 | 3.2 | 0 | 0 | 0 | 0 |  |  | 1
Teff | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63.8 | 112.6 | 9.5 | 0 |  |  | 2
Wheat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 58.7 | 120.4 | 107.1 | 32.4 |  |  | 3
Barley | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1 | 52.8 | 14.5 | 0 | 0 |  |  | 4
Flax | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 8.4 | 70.2 | 75.6 | 0 | 0 |  |  | 5
Beans_Peas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6 | 55.8 | 6.9 | 0 | 0 |  |  | 6
Garlic | 91.8 | 107.4 | 69.2 | 0 | 0 | 0 | 0 | 0 | 0 | 24.4 | 72 | 87.3 |  |  | 7
Potato | 137.5 | 131.1 | 97.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.6 | 83 |  |  | 8
Cabbage | 88.6 | 86.8 | 83.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.4 | 76.9 |  |  | 9
Carrot/Beet root | 112.3 | 126 | 99.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.6 | 62.2 |  |  | 10
Pepper | 124.6 | 117.6 | 29.6 | 0 | 0 | 0 | 0 | 0 | 0 | 19.4 | 52.3 | 97.7 |  |  | 11
Beans_Peas 2 | 129.7 | 66.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.4 | 68.2 | 122.5 |  |  | 12
Maize 2 | 131.2 | 124.7 | 71.5 | 0 | 0 | 0 | 0 | 0 | 0 | 19.4 | 52.7 | 102 |  |  | 13
Nr of days/month | 31 | 28 | 31 | 30 | 31 | 30 | 31 | 30 | 31 | 31 | 30 | 31
Net scheme irr.req.
(mm/day) | 1.8 | 2 | 1.1 | 0 | 0.1 | 0.1 | 0 | 0 | 0.9 | 1.6 | 1.3 | 1.5
(mm/month) | 57.3 | 54.9 | 33.3 | 0.5 | 1.7 | 1.7 | 0 | 1.3 | 27.9 | 48.6 | 38.2 | 47.1
(l/s/h) | 0.21 | 0.23 | 0.12 | 0 | 0.01 | 0.01 | 0 | 0 | 0.11 | 0.18 | 0.15 | 0.18
Irrigated area (%) | 49 | 49 | 44 | 5 | 5 | 10 | 0 | 27 | 45 | 74 | 82 | 59
Net sutable irrigation area (ha) | J: 257.4918
Net actual area to be irrigated (ha) | 126.171 | 126.171 | 113.2964 | 12.8746 | 12.8746 | 25.7492 | 0 | 69.5228 | 115.8713 | 190.5439 | 211.1433 | 151.9202
Irr.req. for actual area (l/s/h) for 24hr | 0.44 | 0.46 | 0.28 | 0.04 | 0.13 | 0.06 | 0 | 0.02 | 0.24 | 0.25 | 0.18 | 0.3
Irr.req. for actual area after 60% project efficiency (l/s/h) for 24hr | 0.73333 | 0.76667 | 0.46667 | 0.066667 | 0.21667 | 0.1 | 0 | 0.033333 | 0.4 | 0.41667 | 0.3 | 0.5
Demand
Irrigation demand (l/s) | 92.5254 | 96.7311 | 52.8717 | 0.85831 | 2.7895 | 2.5749 | 0 | 2.3174 | 46.3485 | 79.3933 | 63.343 | 75.9601
Irrigation demand (m3/s) for 24hr | 0.092525 | 0.096731 | 0.052872 | 0.00085831 | 0.0027895 | 0.0025749 | 0 | 0.0023174 | 0.046349 | 0.079393 | 0.063343 | 0.07596
Irrigation demand (Mm3) | 0.24782 | 0.23401 | 0.14161 | 0.0022247 | 0.0074714 | 0.0066742 | 0 | 0.0060068 | 0.12414 | 0.21265 | 0.16419 | 0.20345 | 1.3502
Irrigation demand including 10% future demand (m3/s) | 0.2726 | 0.25741 | 0.15577 | 0.0024472 | 0.0082185 | 0.0073416 | 0 | 0.0066074 | 0.13655 | 0.23391 | 0.1806 | 0.2238 | 1.4853
Peak water supply demand by 2040, (Mm3) | 0.1607 | 0.14515 | 0.1607 | 0.15552 | 0.1607 | 0.15552 | 0.1607 | 0.15552 | 0.1607 | 0.1607 | 0.15552 | 0.1607 | 1.8922
Total demand, (Mm3) | 0.43331 | 0.40257 | 0.31648 | 0.15797 | 0.16892 | 0.16286 | 0.1607 | 0.16213 | 0.29726 | 0.39462 | 0.33612 | 0.3845 | 3.3774
Monthly low flow/Supply
Base flow from Kerkero (m3/s) | 0.75 | 0.375 | 0.21 | 0.12 | 0.22642 | 0.47893 | 0.72704 | 0.64853 | 0.32426 | 0.16213 | 0.081066 | 0.040533
Base flow from Bollo (m3/s) | 0.0675 | 0.03375 | 0.03375 | 0.03375 | 0.25083 | 0.53058 | 0.80544 | 0.71846 | 0.35923 | 0.17961 | 0.089807 | 0.044904
Total Supply (m3/s) | 0.8175 | 0.40875 | 0.24375 | 0.15375 | 0.47725 | 1.0095 | 1.5325 | 1.367 | 0.68349 | 0.34175 | 0.17087 | 0.085436
Monthly low flow/Supply (Mm3) | 2.1896 | 0.98885 | 0.65286 | 0.39852 | 1.2783 | 2.6167 | 4.1046 | 3.5432 | 1.8307 | 0.91533 | 0.4429 | 0.22883 | 19.1903
Water Balance (Mm3) | 1.7563 | 0.58628 | 0.33638 | 0.24055 | 1.1093 | 2.4538 | 3.9439 | 3.3811 | 1.5334 | 0.52072 | 0.10678 | -0.15567 | 15.8128
Expected irrigation supply from Kerkero River for 24hr (m3/s) | 0.025025 | 0.062981 | 0.019122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.031057
Expected irrigation supply from Kerkero River for 24hr (Mm3), 26.2% | 0.067028 | 0.15236 | 0.051215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.083182 | 0.35379 | 26.2%
|  |  |  | 0.1875 | 80.62%

## Supply
Parameter | Value
Supply | J | F | M | A | M | J | J | A | S | O | N | D
Base flow from Kerkero, m3/s | 0.75 | 0.375 | 0.21 | 0.12 | 0.22642 | 0.47893 | 0.72704 | 0.64853 | 0.32426 | 0.16213 | 0.081066 | 0.040533
Base flow from Bollo, m3/s | 0.0675 | 0.03375 | 0.03375 | 0.03375 | 0.25083 | 0.53058 | 0.80544 | 0.71846 | 0.35923 | 0.17961 | 0.089807 | 0.044904
Demand
Water Duty (l/s)
Net irrigation area (ha) | Value J: 257.4918
Peak annual demand for the next 15 years (l/s) | Value J: 60
Ambo Water Supply Location
| X | Y | Z
| 378657.412 | 988511.762 | 2268

## Design of pump
Table: Design of pump for BK SSIP
Item description | Value | Unit | Remark |  | NB: There are two MCs in consequetive, the first part runs from BSR to intake on Bollo River & the second starts from this intake and supply majority of the command area
I. Project Site and Studied data |  |  |  |  | Thus, supply is from two sources: Bollo River and Kerkero River. Bollo River has a base flow of 60 l/s and Kerkero River pumps are designed for supplying the balance from Kerkero River
Project Demand data |  |  |  |  | Note: X-section of pipe is to be taken from source to balancing storage independently
Peak irrigation duty for 24hrs per day, | 0.76667 | l/s/ha | collected from CWR
Peak irrigation duty for pump operation hrs per day, | 1.84 | l/s/ha | Expected to operate for 10hrs/day
Gross command Area = | 373.9 | ha
Expected infrastructure & unsuitable Area = | 116.4082 | ha | Extracted from layout map
Net command Area = | 257.4918 | ha
Required discharge for net command area for 10hrs/day | 0.47378 | m3/s | Q = q*A if all are supplied at a time in 10hrs/day
Available Base flow in Bollo River | 0.0675 | m3/s | Expected to operate for 24hrs/day
Thus, max. discharge to be pumped from Kerkero River | 0.15115 | m3/s | By two pupms operating at a time for 10hrs/day
Project Site data
Existing river bed elevation | 2511.7155 | m
Measured depth of minimum water in the river, d' | 0.7 | m
Sump hole below RBL | 1 | m
Safe minimum water level | 2512.4155 | m
Observed Flood mark level at Headwork | 2513.11 | m
Suction pipe axis | 2515.2505 | m | Pump center line level
Suction pipe axis above MFL | 2.1405 | m
OGL on d/s side of reservoir | 2546 | m
OGL on u/s side of reservoir | 2549 | m
Delivery pipe axis outlet | 2549.5 | m | Avg. OGL + assumed tank ht
II. Determination of Pump Hydraulics
Suction side
Pipe Material | GS/DCI
Avg. temp. at project site (from Hydrology) = | 20 | oc
Altitude at the project site | 2515.2505 | m | Pump center line level
Suction pipe length, Ls = | 7.835 | m | 3 parallel pipes of each this much length
Total number of pumps required | 3 | Nr | 2 operating & 1 standby pump
Discharge per each operating pumps at a time | 0.075577 | m3/s | 280 |  |  | Pumping Head
Allowed flow velocity in suction pipe, V = | 1.6 | m/s
Calculated diameter of each suction pipe, d = | 0.24297 | m
Adopted diameter of suction pipeline, ds = | 0.25 | m
Velocity head in suction side, ha = V2/2g | 0.13048 | m
Hazen-Williams eqn for Head loss in pipe lines | 0.12755 | m
Hazen-Williams roughness coefficient for steel pipe, C = | 100
Suction pipe to be submerged 4ds = | 1 | m | Thus, sump hole depth= d'+4ds = 1.7m
Loss due to bend/ bend loss, = Kb * v2/2g, where Kb =0.19, thus loss = | 0.024791 | m
Suction lift head= Suction pipe axis level - Safe minimum water level = | 2.835 | m
Strainer + valve loss= Ks * v2/2g, where Ks =2, thus loss = | 0.26096 | m
Entry loss = Ke * v2/2g, where Ke =0.1, thus loss = | 0.013048 | m
Hence, minor head loss on suction side (m) = Frictional loss + bend loss + (strainer + Valve) loss + Entry loss = | 0.42635 | m
Total Suction Head, Hs = Suction lift head + minor Head loss = | 3.2614 | m
NPSHa = Ha – Hf – Hs – es – Fs |  | m
Ha - is atmospheric pressure at water surface | 10.33 | m
Thus, net available atm. Press. Ha = | 7.3117 | m | Corr. factor = - 0.36m/300m altitude,
Vapour Pressure at project Site, | 0.23362 | m
Where, ed is in mbar and Ts is in 0C
Fs - is factor of safety = | 0.6 | m
Thus NPSHa = | 2.5155 | m
Required Net positive suction head (NPSHR) is provided by the manufacture but for safety of the designed pump, the absolute head at the pump inlet must be calculated as:
NPSHR = (Ha – HVp)/Pg Where, |  |  |  |  | 1mbar = |  | 0.001 | bar
Ha = atmospheric pressure at inlet (minimum water surface) | 7.3117 | m |  |  | 1bar = |  | 10 | m
Pv = Vapor pressure at the give temperature ºc | 0.23362 | m |  |  | Thus, 1mbar = |  | 0.01 | m
P = Specific gravity at a given temp for the project site= | 0.998 | m
g = gravitation due to acceleration = | 9.81 | m
Thus, absolute head at pump inlet = | 0.72296 | m
Deducting S.F from this value will give, NPSHR = | 0.12296 | m
Now, check against cavitation by comparing NPSHr & NPSHa | Ok! |  | If NPSHr < NPSHa, there is no cavitation
NPSHa should also satisfy minimum requirement, i.e. NPSHa > 2.0 | Ok!
Delivery side
Pipe Material | UPVC
Pipe length, b/n pump axis and Delivery pipe axis outlet, Ld = | 120 | m
Delivery pipe axis outlet level | 2549.5 | m
Static delivery head, Hd | 34.2495 | m
Allowed velocity at out of delivery pipe, Vd = | 2 | m/s
Assume single Delivery pipe, thus Discharge = 2*That of suction side | 0.15115 | m3/s
Calculated diameter of each suction pipe, d = | 0.31021 | m
Adopted diameter of delivery pipeline, ds = | 0.35 | m
Velocity head in delivery side, ha = V2/2g | 0.20387 | m
Cheek valve loss, hcv= Kcv * V2/2g, where Kcv =0.8, thus loss = | 0.1631 | m
Hazen-Williams roughness coefficient for UPVC pipe, C = | 140 |  | Assumed new pipe
Hazen-Williams eqn for Head loss in pipe lines | 1.0683 | m
Exit loss, = Ke * V2/2g, where Ke =1, thus loss = | 0.20387 | m
Loss due to bend/ bend loss, hb= Kb * v2/2g, where Kb =0.19, thus loss = | 0.11621 | m | At three points:
Total head loss in delivery pipeline, hd = | 1.5515 | m | hd = ha + hcv + Hf + hb
Hence, Total Delivery Head = Static head + Total Head loss | 35.801 | m
Thus, Total Pumping Head, Ht = | 39.0624 | m | Ht = Hs + Hd
Adopted Total Pumping Head, Ht = | 40 | m
III. Determination of pump capacity
Required power, P = QHt/hphm |  | KW
Where, Ht = Total head in the system (m) | 40 |  |  |  |  | 1KVA = | 0.8 | KW
Q = Discharge per pump (lit /s) | 75.5773 |  |  |  |  | 1KW = | 1.34 | HP
Thus, Required power, P = | 50 | KW |  |  |  | 1KVA = | 1.072 | HP
Brake horse power (BHP) =WHP/ hpm =
Where, hpm = Efficiency of Coupled pump and motor | 0.49 |  | if diesel
| 0.595 |  | if electric
Thus, Power required to operate the system, P (KW)= | 50 | KW | if electric
| 65 | KW | if diesel
Thus, Power required to operate the system, P (HP)= | 70 | HP | if electric
| 85 | HP | if diesel
IV/ Decision
Provide two operating pumps and one standby pump with capacities of P = 70HP/50KW if electric or 80HP/55KW if diesel; Total Pumping Head, Ht =40m & discharge capacity of 76 l/s or 275m3/hr each. Efficiency of Coupled pump and motor will be 65% if electric or 56% if diesel
V/ Operation Schedule of Pumps
|  |  | Operation hours | Operation Frequency |  |  | Operation Hours (Hrs/day) |  |  | All Pumps
|  |  |  | Pump1 | Pump2 | Pump3 | Pump1 | Pump2 | Pump3
Day-1
|  |  | 7:00 am to 12:00 am | Ö | X | Ö | 5 | 0 | 5 | 10
|  |  | 01:00 pm - 06:00 pm | X | Ö | Ö | 0 | 5 | 5 | 10
|  |  | Sub Total | Once/day | Once/day | tiwice/day | 5hrs/day | 5hrs/day | 10hrs/day | 20 hrs/day
Day-2
|  |  | 7:00 am to 12:00 am | Ö | Ö | X | 5 | 5 | 0 | 10
|  |  | 01:00 pm - 06:00 pm | Ö | X | Ö | 5 | 0 | 5 | 10
|  |  | Sub Total | tiwice/day | tiwice/day | Once/day | 10hrs/day | 8hrs/day | 5hrs/day | 20 hrs/day
Day-3
|  |  | 7:00 am to 12:00 am | Ö | Ö | X | 5 | 5 | 0 | 10
|  |  | 01:00 pm - 06:00 pm | X | Ö | Ö | 0 | 5 | 5 | 10
|  |  | Sub Total | Once/day | tiwice/day | Once/day | 5hrs/day | 10hrs/day | 5hrs/day | 20 hrs/day
Day-4
Same schedule holds true then after i.e. pumps operating in day-1 will repeat here & so on.
Note on B19: preffered user: Bank Level + 0.5
Note on B23: preffered user: OGL=2549 but on d/s side = 2546
Note on B29: preffered user: 4m is horizontal length, & 1m just for creating pool and/or avoiding silt
Note on B31: preffered user: 1 standby pump
Note on B76: preffered user: 3 is expected Nr of bends at collection chamber

## O&M Costs of pump
Description | Value | Unit | Remark
Discharge, Q of each pump, l/s | 75.5773 | or | 0.075577 | m3/sec
Number of pumps operating at a time | 2
Total dynamic head, H= |  |  | 40 | m
Power of pump, P if electric | 50 | KW | 67.051 | say 70HP | Efficiencies of pump and motor
Power of pump, P if diesel | 65 | KW | 87.1663 | say 75HP | Pump by | Proposed (%) |  | Adopted (%) |  | if coupled
[6 empty] | e1 | e2 | e1 | e2 | e
Table: Estimated Power Requirement of Pumps |  |  |  |  | Electric | 0.5-0.8 | 0.7-0.95 | 0.7 | 0.85 | 0.595
Description | Value | Unit | Remark |  | Diesel | 0.5-0.8 | 0.65-0.80 | 0.7 | 0.7 | 0.49
Power requirement if electric | 50 | KW | or 70 HP
Power requirement if diesel | 65 | KW | or 75 HP |  | 1 | l/s = | 3.6 | m3/hr
Cost of electricity = | 0.8 | ETB/kWh
Cost of diesel fuel = | 20 | ETB/lit | Rate expected on-site
Energy cost per hour =
- electric | 40 | ETB/hr
- diesel | 1300 | ETB/hr
Specific energy of diesel fuel = | 11 | KWh/lit | Adopted from Megech
Therefore, diesel fuel requirement = | 5.9091 | lit/hour
Volume of water pumped per hour = | 544.1567 | m3/hr | 1l/s=3.6m3/hr | 2 pumps
Peak gross irrigation requirement | 1.84 | l/s/ha | Overall effi.=45%
Net area to be irrigated | 257.4918 | ha | by pump
Gross water requirement for this area = | 1.3502 | Mm3 | For peak condition
Gross water requirement from Kerkero alone = | 0.35379 | Mm3
Annual gross depth of irrig. req'd in the field= | 137.3982 | mm | This is peak reqiurement
Gross water requirement/hectare = | 1373.9819 | m3/ha | from Kerkero alone
Total pumping hours per season/year= | 650.1604 | hrs
Energy cost/ha per season/year =
- if electric | 100.999 | ETB/ha
- if diesel | 3282.4672 | ETB/ha
Total Energy consumption (for peak per season)
- if electric | 60000 | KWh | For 120 days & 10hr/day
- if diesel | 87750 | KWh
Total Energy cost (for peak demand per season)
- if electric | 48000 | ETB
- if diesel | 159545.4545 | ETB
Maintenance cost required per season
- if electric | 16000 | ETB | 2% of pump cost
- if diesel | 16000 | ETB
Total O&M cost (for peak demand per season)
- if electric | 64000 | ETB
- if diesel | 175545.4545 | ETB
Operators (#2 per season) | 18000 | ETB | Assumed 1000 ETB/month
Guards (#2 per season) | 24000 | ETB | Assumed 800 ETB/month
G.Total O&M cost (for peak demand/season)
- if electric | 106000 | ETB | For two seasons i.e. 1 yr
- if diesel | 217545.4545 | ETB
Assumed Nr of project beneficiary households | 100 | HH | By household heads
O&M share of each household head/season
| 1060 | ETB/HH | Operation cost/HH/yr
| 2175.4545 | ETB/HH | Operation cost/HH/yr
Note on B2: preffered user: 2 pupms operating at a time

## Area+TU1
Table: Area by Tertiary Units (ha) | [18 empty] | Table: Analysis of Senario for Potential Area Developement
MC |  |  | SC |  |  | TC |  |  | FC |  |  |  | q24hr = | 0.76667 |  |  |  |  | Item | Full Irrigation | Supplementary Irrigation
Name | Area, ha | Leng (km) | Name | Area, ha | Leng (km) | Name | Area, ha | Leng (km) | Name | Area, ha |  | Options of Irrigation application duration | [6 empty] | Peak Duty, q24 (l/s/ha) | 0.76667 | 0.5
MC1 | 29.4501 | 1.6287 | SC1 | 5.851 | 0.10282 | TC1-1 | 1.5496 | 0.11371 | FC1-1-1 | 1.0317 |  | Item | Duration Option (hr) | [5 empty] | q10 (l/s/ha) | 1.84 | 1.2
[9 empty] | FC1-1-2 | 0.5179 |  | Flow duration in MC2/MC1 | 24/10 | 24/10 | 24/10 | 24/10 | 24/10 | 24/10 | q14 (l/s/ha) | 1.3143 | 0.85714
[6 empty] | TC1-2 | 1.5003 | 0.08867 | FC1-2-1 | 0.72055 |  | If Irrigation duration, (hr) | 1 | 3 | 5 | 10 | 12 | 24 | Discharge, Q (l/s) | 151 | 151
[9 empty] | FC1-2-2 | 0.77978 |  | Peak Flow Rates, q (l/s/ha) | 18.4 | 6.1333 | 3.68 | 1.84 | 1.5333 | 0.76667 | Discharge, Q (l/s) | #REF! | 67.5
[9 empty] | FC0-1-1 | 0.78226 |  | Max Area to be irrigated | [6 empty] | Area that can be developed by pump, A1 (ha) | 82.0652 | 125.8333
[9 empty] | FC0-1-2 | 2.0188 |  | from Ker+Bollo |  |  |  | 82.1493 |  |  | Area that can be developed from Bollo during 10 hrs, A2 (ha) | #REF! | 56.25
|  |  | Subtotal SC1 | 5.851 | 0.10282 |  | 3.05 | 0.20238 |  | 5.851 |  | from Bollo alone |  |  |  | 36.6848 |  |  | Area that can be developed from Bollo during 14 hrs, A3 (ha) | #REF! | 78.75
|  |  | SC2 | 23.5991 | 0.24178 | TC2-1 | 3.7092 | 0.09551 | FC2-1-1 | 1.9168 |  | Table: Discharge statement of MCs & SCs | [6 empty] | Total Area that can be developed from all options (ha) | #REF! | 260.8333
[9 empty] | FC2-1-2 | 1.7924 |  | Name | Leng (km) | Net Area |  | Required Q, m3/s | Balance for storage | Remark | Note: Though maximum area that can be developed by the measured base flow during supplementary Irrigation shows 260.8ha in this table, we took the identified net area of 257.5 ha for canal design. Thus, the most d/s of 126 ha is to be irrigated only in supplementary.
[6 empty] | TC2-2 | 7.2535 | 0.30189 | FC2-2-1 | 2.5954 |  |  |  | (ha) | % | [5 empty] | #REF!
[9 empty] | FC2-2-2 | 2.6229 | 126.4475 | MC1 | 1.6287 | 29.4501 | 11.44% | 0.15115 |  | To be stored for a max. of 10 hrs in BSR |  |  | Thus areas for full irrigation are:
[9 empty] | FC2-2-3 | 2.0351 |  | MC2 | 2.4781 | 228.0417 | 88.56% | 0.1849 |  | Max. MC capacity |  |  | Areas of SC1 | 5.851
[6 empty] | TC2-3 | 4.7373 | 0.12566 | FC2-3-1 | 1.9147 |  | Subtotal MC1 & MC1 | 4.1068 | 257.4918 | 100% | [5 empty] | Areas of SC2 | 23.5991
[9 empty] | FC2-3-2 | 2.8226 |  | SC1 |  | 5.851 | 2.272% | 0.010766 |  |  |  |  | Areas of SC3 up to TC3-20 | 81.9991
[6 empty] | TC2-4 | 7.8991 | 0.18214 | FC2-4-1 | 4.8438 |  | SC2 |  | 23.5991 | 9.165% | 0.043422 |  |  |  |  | After of SC3 after NSR2 | 21.2141
[9 empty] | FC2-4-2 | 3.0553 |  | SC3 |  | 121.0316 | 47% | 0.2227 | 0.037794 | To be stored in NSR for 14 hrs |  |  | Subtotal for full irrigation | 132.6634
|  |  | Subtotal SC2 | 23.5991 | 0.24178 |  | 23.5991 | 0.7052 |  | 23.5991 |  | SC4 |  | 57.4048 | 22.29% | 0.10562
Subtotal MC1 | 29.4501 | 1.6287 |  | 29.4501 | 0.3446 |  | 26.6491 | 0.90758 |  | 29.4501 |  | SC5 |  | 31.787 | 12.34% | 0.058488
MC2 | 228.0417 | 2.4781 | SC3 | 121.0316 | 2.4722 | TC3-1 | 6.088 | 0.12909 | FC3-1-1 | 2.7368 |  | SC6 |  | 14.4011 | 5.593% | 0.026498
[9 empty] | FC3-1-2 | 3.3512 |  | Subtotal SCs |  | 254.0746 | 98.67%
[6 empty] | TC3-2 | 3.8552 | 0.13953 | FC3-2-1 | 2.2942 |  | Areas by TC & FC from MC |  | 3.4172 | 1.327%
[9 empty] | FC3-2-2 | 1.5611 |  | Total |  | 257.4918 | 100%
[6 empty] | TC3-3 | 3.4301 | 0.13793 | FC3-3-1 | 1.562
[9 empty] | FC3-3-2 | 1.8681
[9 empty] | FC3-0-1 | 2.1008 |  | Name | Gross Area |  | Net Area |  | Remark
[6 empty] | TC3-4 | 3.3105 | 0.12886 | FC3-4-1 | 1.7113 |  |  | (ha) | % | (ha) | %
[9 empty] | FC3-4-2 | 1.5991 |  | MC1 | 76.98 | 20.59% | 29.4501 | 11 | Majority of the studied areas are excluded due to topography
[9 empty] | FC3-0-2 | 1.445 |  | MC2 | 296.89 | 79.41% | 228.0417 | 89
[6 empty] | TC3-5 | 2.8866 | 0.12868 | FC3-5-1 | 1.4243 |  | Total | 373.87 | 100% | 257.49 | 100
[9 empty] | FC3-5-2 | 1.4623
[9 empty] | FC3-0-3 | 1.5916
[6 empty] | TC3-6 | 3.7199 | 0.12543 | FC3-6-1 | 1.9021
[9 empty] | FC3-6-2 | 1.8178
[9 empty] | FC3-0-4 | 2.3962
[6 empty] | TC3-7 | 3.1457 | 0.13197 | FC3-7-1 | 1.7499
[9 empty] | FC3-7-2 | 1.3958
[9 empty] | FC3-0-5 | 2.1743
[6 empty] | TC3-8 | 2.8566 | 0.14913 | FC3-8-1 | 1.6971
[9 empty] | FC3-8-2 | 1.1595
[9 empty] | FC3-0-6 | 2.5709
[6 empty] | TC3-9 | 3.1959 | 0.14391 | FC3-9-1 | 1.6551
[9 empty] | FC3-9-2 | 1.5408
[9 empty] | FC3-0-7 | 3.1885
[6 empty] | TC3-10 | 2.941 | 0.13007 | FC3-10-1 | 1.5752
[9 empty] | FC3-10-2 | 1.3658
[6 empty] | TC3-11 | 3.9073 | 0.12681 | FC3-11-1 | 1.589
[9 empty] | FC3-11-2 | 2.3183
[6 empty] | TC3-12 | 2.5026 | 0.12597 | FC3-12-1 | 1.5099
[9 empty] | FC3-12-2 | 0.99261
[6 empty] | TC3-13 | 3.9067 | 0.12731 | FC3-13-1 | 1.5132
[8 empty] | 0.35557 | FC3-13-2 | 2.3935
[6 empty] | TC3-14 | 2.8451 | 0.13159 | FC3-14-1 | 1.4904
[8 empty] | 1.3556 | FC3-14-2 | 1.3546
[6 empty] | TC3-15 | 3.4627 | 0.12689 | FC3-15-1 | 1.4941
[8 empty] | 2.3556 | FC3-15-2 | 1.9686
[6 empty] | TC3-16 | 2.9546 | 0.12881 | FC3-16-1 | 1.5069
[8 empty] | 3.3556 | FC3-16-2 | 1.4477
[6 empty] | TC3-17 | 3.2987 | 0.12624 | FC3-17-1 | 1.4245
[8 empty] | 4.3556 | FC3-17-2 | 1.8742
[6 empty] | TC3-18 | 3.0442 | 0.12737 | FC3-18-1 | 1.5411
[8 empty] | 5.3556 | FC3-18-2 | 1.5031
[6 empty] | TC3-19 | 2.0876 | 0.12672 | FC3-19-1 | 1.2828
[8 empty] | 6.3556 | FC3-19-2 | 0.80481
[6 empty] | TC3-20 | 3.0928 | 0.13248 | FC3-20-1 | 1.6183
[8 empty] | 6.3556 | FC3-20-2 | 1.4744
[9 empty] | FC3-0-8 | 2.8201
[6 empty] | TC3-21 | 2.5368 | 0.13724 | FC3-21-1 | 1.4858
[9 empty] | FC3-21-2 | 1.0509
[6 empty] | TC3-22 | 2.9684 | 0.11739 | FC3-22-1 | 1.3367
[9 empty] | FC3-22-2 | 1.6317
[6 empty] | TC3-23 | 3.1668 | 0.14979 | FC3-23-1 | 1.87
[9 empty] | FC3-23-2 | 1.2968
[6 empty] | TC3-24 | 3.2951 | 0.11692 | FC3-24-1 | 1.4297
[9 empty] | FC3-24-2 | 1.8654
[6 empty] | TC3-25 | 3.0311 | 0.15345 | FC3-25-1 | 1.9802
[9 empty] | FC3-25-2 | 1.0509
[6 empty] | TC3-26 | 3.3329 | 0.11941 | FC3-26-1 | 1.4091
[9 empty] | FC3-26-2 | 1.9239
[6 empty] | TC3-27 | 2.6521 | 0.14573 | FC3-27-1 | 1.6207
[9 empty] | FC3-27-2 | 1.0313
[6 empty] | TC3-28 | 3.9016 | 0.12373 | FC3-28-1 | 1.4553
[9 empty] | FC3-28-2 | 2.4462
[6 empty] | TC3-29 | 2.4551 | 0.14968 | FC3-29-1 | 1.628
[9 empty] | FC3-29-2 | 0.82712
[9 empty] | FC3-0-9 | 2.5832
[6 empty] | TC3-30 | 3.7842 | 0.15716 | FC3-30-1 | 2.3297
[9 empty] | FC3-31-2 | 1.4545
[9 empty] | FC3-0-10 | 2.505
|  |  | Subtotal SC3 | 121.0316 | 2.4722 |  | 97.6558 | 33.8398 |  | 121.0316
|  |  | SC4 | 57.4048 | 1.6374 |  |  |  | FC4-0-0 | 0.18086
[6 empty] | TC4-1 | 2.5071 | 0.09154 | FC4-1-1 | 1.3203
[9 empty] | FC4-1-2 | 1.1868
[9 empty] | FC4-0-1 | 1.3133
[6 empty] | TC4-2 | 2.7151 | 0.12329 | FC4-2-1 | 1.4893
[9 empty] | FC4-2-2 | 1.2257
[9 empty] | FC4-0-2 | 1.9694
[6 empty] | TC4-3 | 2.903 | 0.12542 | FC4-3-1 | 1.5105
[9 empty] | FC4-3-2 | 1.3925
[9 empty] | FC4-0-3 | 2.6708
[6 empty] | TC4-4 | 3.5491 | 0.12845 | FC4-4-1 | 1.539
[9 empty] | FC4-4-2 | 2.0101
[9 empty] | FC4-0-4 | 2.8176
[6 empty] | TC4-5 | 3.1628 | 0.12785 | FC4-5-1 | 1.5492
[9 empty] | FC4-5-2 | 1.6136
[9 empty] | FC4-0-5 | 2.5384
[9 empty] | FC4-0-6 | 2.4284
[9 empty] | FC4-0-7 | 2.4969
[9 empty] | FC4-0-8 | 1.5162
[9 empty] | FC4-0-9 | 2.2351
[9 empty] | FC4-0-10 | 1.45
[9 empty] | FC4-0-11 | 1.7388
[9 empty] | FC4-0-12 | 2.0658
[9 empty] | FC4-0-13 | 1.2629
[9 empty] | FC4-0-14 | 2.1929
[9 empty] | FC4-0-15 | 1.5669
[9 empty] | FC4-0-16 | 2.0603
[9 empty] | FC4-0-17 | 2.4625
[6 empty] | TC4-6 | 2.3894 | 0.11012 | FC4-6-1 | 1.3659
[9 empty] | FC4-6-2 | 1.0235
[9 empty] | FC4-0-18 | 2.3495
[6 empty] | TC4-7 | 1.8863 | 0.12615 | FC4-7-1 | 0.8864
[9 empty] | FC4-7-2 | 0.99989
[9 empty] | FC4-0-19 | 0.97552
|  |  | Subtotal SC4 | 57.4048 | 1.6374 |  | 19.1127 | 0.83282 |  | 57.4048
[6 empty] | TC0-1 | 1.8619 | 0.16 | FC0-1-1 | 0.92862
[9 empty] | FC0-1-2 | 0.93323
|  |  | Subtotal TC0 |  |  |  | 1.8619 | 0.16 |  | 1.8619
|  |  | SC5 | 31.787 | 0.18257 | TC5-1 | 4.4213 | 0.32712 | FC5-1-1 | 1.9555
[9 empty] | FC5-1-2 | 1.1213
[9 empty] | FC5-1-3 | 1.3445
[9 empty] | FC5-0-1 | 1.87
[6 empty] | TC5-2 | 5.7613 | 0.29755 | FC5-2-1 | 1.9463
[9 empty] | FC5-2-2 | 1.4979
[9 empty] | FC5-2-3 | 2.3171
[9 empty] | FC5-0-2 | 2.3748
[6 empty] | TC5-3 | 3.4485 | 0.16503 | FC5-3-1 | 1.9133
[9 empty] | FC5-3-2 | 1.5352
[9 empty] | FC5-0-3 | 1.9012
[6 empty] | TC5-4 | 3.7602 | 0.18786 | FC5-4-1 | 2.1653
[9 empty] | FC5-4-2 | 1.5949
[9 empty] | FC5-0-4 | 1.9712
[6 empty] | TC5-5 | 2.3139 | 0.144 | FC5-5-1 | 1.5123
[9 empty] | FC5-5-2 | 0.80155
[9 empty] | FC5-0-5 | 1.8967
[9 empty] | FC5-0-6 | 1.2194
[9 empty] | FC5-0-7 | 0.84856
|  |  | Subtotal SC5 | 31.787 | 0 |  | 19.7051 | 1.1216 |  | 31.787
[9 empty] | FC0-0-1 | 1.5554
|  |  | Subtotal |  |  |  | 0 | 0 |  | 1.5554
|  |  | SC6 | 14.4011 | 0.18257 |  |  |  | FC6-0-1 | 0.52261
[6 empty] | TC6-1 | 2.6682 | 0.10282 | FC6-1-1 | 1.44
[9 empty] | FC6-1-2 | 1.2282
[6 empty] | TC6-2 | 3.7905 | 0.10282 | FC6-2-1 | 1.6661
[9 empty] | FC6-2-2 | 2.1244
[6 empty] | TC6-3 | 4.2397 | 0.10282 | FC6-3-1 | 2.0859
[9 empty] | FC6-3-2 | 2.1538
[6 empty] | TC6-4 | 3.18 | 0.10282 | FC6-4-1 | 1.9718
[9 empty] | FC6-4-2 | 1.2082
|  |  | Subtotal SC6 | 14.4011 | 0.18257 |  | 13.8784 | 0.4113 |  | 14.4011
Subtotal MC2 | 228.0417 | 2.4781 |  | 224.6245 | 4.2921 |  | 152.214 | 36.3655 |  | 228.0417
Grand Total | 257.4918 | 4.1068 |  | 254.0746 | 4.6367 |  | 178.863 | 37.2731 |  | 257.4918
Study/Gross area= | 373.9 |  |  |  | Nr of TC | 53 |  |  | Nr of FC | 150
[5 empty] | TC on MC1 | 6 |  |  | FC on MC1 | 15
[5 empty] | TC on MC2 | 47 |  |  | FC on MC2 | 135
[9 empty] | Max | 4.8438
[9 empty] | Min | 0.18086
1.7166
Note on Y7: preffered user: measured